## EC
STANDARD
EC.01.01.01 | [6 empty] | The hospital plans activities to minimize risks in the environment of care. Note: One or more persons can be assigned to manage risks associated with the management plans described in this standard. Rationale: Risks are inherent in the environment because of the types of care provided and the equipment and materials that are necessary to provide that care. The best way to manage these risks is through a systematic approach that involves the proactive evaluation of the harm that could occur. By identifying one or more individuals to coordinate and manage risk assessment and reduction activities—and to intervene when conditions immediately threaten life and health—organizations can be more confident that they have minimized the potential for harm. Risks in the environment include safety and security for people, equipment, and other material; the handling of hazardous materials and waste; the potential for fire; the use of medical equipment; and utility systems. High-level written management plans help the hospital manage risks. These plans are not the same as operational plans, but they do provide a framework for managing the environment of care. These plans should also address the scope and objectives of risk assessment and management, describe the responsibilities of individuals or groups, and give time frames for specific activities identified in the plan. Note: It is not necessary to have a separate plan for each of the areas identified in the standard; the plans may all be contained in a single document. Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
[5 empty] | A | ESP-1 | 1. Leaders identify an individual(s) to manage risk, coordinate risk reduction activities in the physical environment, collect deficiency information, and disseminate summaries of actions and results. Note: Deficiencies include injuries, problems, or use errors.
[5 empty] | A | ESP-1 | 2. Leaders identify an individual(s) to intervene whenever environmental conditions immediately threaten life or health or threaten to damage equipment or buildings.
| §482.26(b) §482.41(a) |  |  | D | A | ESP-1 | 3. The hospital has a written plan for managing the following: The environmental safety of patients and everyone else who enters the hospital’s facilities. (See also EC.04.01.01, EP 15)
| §482.13(c)(2) |  |  | D | A | ESP-1 | 4. The hospital has a written plan for managing the following: The security of everyone who enters the hospital’s facilities. (See also EC.04.01.01, EP 15)
| §482.26(b) §482.41(a) |  |  | D | A | ESP-1 | 5. The hospital has a written plan for managing the following: Hazardous materials and waste. (See also EC.04.01.01, EP 15)
| §482.41(a) |  |  | D | A | ESP-1 | 6. The hospital has a written plan for managing the following: Fire safety. (See also EC.04.01.01, EP 15)
| §482.41(a) §482.41(c)(2) |  |  | D | A | ESP-1 | 7. The hospital has a written plan for managing the following: Medical equipment. (See also EC.04.01.01, EP 15)
| §482.41(a) §482.41(c)(2) |  |  | D | A | ESP-1 | 8. The hospital has a written plan for managing the following: Utility systems. (See also EC.04.01.01, EP 15)
STANDARD
EC.02.01.01 | [6 empty] | The hospital manages safety and security risks. Rationale: Safety and security risks are present in most health care environments. These risks affect all individuals in the organization—patients, visitors, and those who work in the hospital. It is important to identify these risks in advance so that the hospital can prevent or effectively respond to incidents. In some organizations, safety and security are treated as a single function, although in others they are treated as separate functions. Safety risks may arise from the structure of the physical environment, from the performance of everyday tasks, or from situations beyond the hospital’s control, such as the weather. Safety incidents are most often accidental. On the other hand, security incidents are often intentional. Security protects individuals and property against harm or loss. Examples of security risks include workplace violence, theft, infant abduction, and unrestricted access to medications. Security incidents are caused by individuals from either outside or inside the hospital. Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.13(c)(2) §482.26(b) §482.41(a) |  |  |  | A |  | 1. The hospital identifies safety and security risks associated with the environment of care that could affect patients, staff, and other people coming to the hospital's facilities. (See also EC.04.01.01, EP 14) Note: Risks are identified from internal sources such as ongoing monitoring of the environment, results of root cause analyses, results of proactive risk assessments of high-risk processes, and from credible external sources such as Sentinel Event Alerts.
| §482.13(c)(2) §482.26(b) §482.41(a) | M | 3 |  | C |  | 3. The hospital takes action to minimize or eliminate identified safety and security risks in the physical environment.
| §482.41(a) | M |  |  | C |  | 5. The hospital maintains all grounds and equipment.
| §482.13(c)(2) |  |  |  | C |  | 7. The hospital identifies individuals entering its facilities. Note: The hospital determines which of those individuals require identification and how to do so.
| §482.13(c)(2) §482.53(b) |  | 3 |  | A |  | 8. The hospital controls access to and from areas it identifies as security sensitive.
| §482.13(c)(2) |  |  | D | A | ESP-1 | 9. The hospital has written procedures to follow in the event of a security incident, including an infant or pediatric abduction. | Yes
| §482.13(c)(2) |  | 3 |  | A |  | 10. When a security incident occurs, the hospital follows its identified procedures.
| §482.25(b) §482.41(a) |  |  |  | C |  | 11. The hospital responds to product notices and recalls. (See also MM.05.01.17, EPs 1–4)
STANDARD
EC.02.01.03 | [6 empty] | The hospital prohibits smoking except in specific circumstances. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
|  |  |  | D | A | ESP-1 | 1. The hospital develops a written policy prohibiting smoking in all buildings. Exceptions for patients in specific circumstances are defined.
[5 empty] | A | ESP-1 | 4. If the hospital decides that patients may smoke in specific circumstances, it designates smoking areas that are physically separate from care, treatment, and service areas. (See also EC.02.03.01, EP 2)
[5 empty] | C |  | 6. The hospital takes action to maintain compliance with its smoking policy.
STANDARD
EC.02.02.01 | [6 empty] | The hospital manages risks related to hazardous materials and waste. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.26(b)(1) §482.41(a) |  |  | D | A | ESP-1 | 1. The hospital maintains a written, current inventory of hazardous materials and waste that it uses, stores, or generates. The only materials that need to be included on the inventory are those whose handling, use, and storage are addressed by law and regulation. (See also IC.02.01.01, EP 6; MM.01.01.03, EP 3)
| §482.26(b) §482.26(b)(1) §482.26(b)(3) §482.41(a) §482.53(b) |  |  | D | A | ESP-1 | 3. The hospital has written procedures, including the use of precautions and personal protective equipment, to follow in response to hazardous material and waste spills or exposures.
| §482.41(a) §482.53(b) |  | 3 |  | A |  | 4. The hospital implements its procedures in response to hazardous material and waste spills or exposures. (See also IC.02.01.01, EP 2)
| §482.41(a) §482.41(b)(6) | M |  |  | C |  | 5. The hospital minimizes risks associated with selecting, handling, storing, transporting, using, and disposing of hazardous chemicals.
| §482.26(b)(1) §482.41(b)(6) §482.53(b) §482.53(b)(2) |  | 3 |  | A |  | 6. The hospital minimizes risks associated with selecting, handling, storing, transporting, using, and disposing of radioactive materials.
| §482.26(b) §482.26(b)(1) §482.26(b)(3) §482.53(b) |  | 3 |  | A |  | 7. The hospital minimizes risks associated with selecting and using hazardous energy sources. Note: Hazardous energy is produced by both ionizing equipment (for example, radiation and x-ray equipment) and nonionizing equipment (for example, lasers and MRIs).
| §482.26(b)(1) §482.41(a) §482.53(b) §482.53(b)(2) |  | 3 |  | C |  | 8. The hospital minimizes risks associated with disposing of hazardous medications. (See also MM.01.01.03, EPs 1-3)
| §482.41(c)(4) | M |  |  | C |  | 9. The hospital minimizes risks associated with selecting, handling, storing, transporting, using, and disposing of hazardous gases and vapors. Note: Hazardous gases and vapors include, but are not limited to, glutaraldehyde, ethylene oxide, vapors generated while using cauterizing equipment and lasers, and gases such as nitrous oxide.
| §482.41(a) |  | 3 |  | A |  | 10. The hospital monitors levels of hazardous gases and vapors to determine that they are in safe range. Note: Law and regulation determine the frequency of monitoring hazardous gases and vapors as well as acceptable ranges.
| §482.26(b)(1) §482.41(a) §482.53(b) §482.53(b)(2) |  |  | D | A | ESP-1 | 11. For managing hazardous materials and waste, the hospital has the permits, licenses, manifests, and safety data sheets required by law and regulation.
| §482.26(b)(1) §482.41(a) §482.53(b) §482.53(b)(2) |  |  |  | A | ESP-1 | 12. The hospital labels hazardous materials and waste. Labels identify the contents and hazard warnings. * (See also IC.02.01.01, EP 6) Footnote *: The Occupational Safety and Health Administration’s (OSHA) Bloodborne Pathogens and Hazard Communications Standards and the National Fire Protection Association (NFPA) provide details on labeling requirements.
| §482.26(b)(3) |  | 3 |  | A | ESP-1 | 18. For hospitals that use Joint Commission accreditation for deemed status purposes: Radiation workers are checked periodically, by the use of exposure meters or badge tests, for the amount of radiation exposure.
| §482.41(b)(6) |  |  |  | A | ESP-1 | 19. For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital has procedures for the proper routine storage and prompt disposal of trash.
STANDARD
EC.02.03.01 | [6 empty] | The hospital manages fire risks. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(b) |  | 3 |  | C | ESP-1 | 1. The hospital minimizes the potential for harm from fire, smoke, and other products of combustion.
|  |  | 3 |  | A |  | 2. If patients are permitted to smoke, the hospital takes measures to minimize fire risk. (See also EC.02.01.03, EP 4)
| §482.41(b) |  | 3 |  | A | ESP-1 | 4. The hospital maintains free and unobstructed access to all exits. Note: This requirement applies to all buildings classified as business occupancy. The "Life Safety" (LS) chapter addresses the requirements for all other occupancy types.
| §482.41(b)(7) |  |  | D | A | ESP-1 | 9. The hospital has a written fire response plan. (See also LS.02.01.70, EP 4)
| §482.41(b)(7) §482.41(b)(1)(i) |  |  |  | A | ESP-1 | 10. The written fire response plan describes the specific roles of staff and licensed independent practitioners at and away from a fire's point of origin, including when and how to sound and report fire alarms, how to contain smoke and fire, how to use a fire extinguisher, and how to evacuate to areas of refuge. (See also EC.02.03.03, EP 5; EC.03.01.01, EP 2; and HR.01.04.01, EP 2) Note: For additional guidance, see NFPA 101, 2000 edition (Sections 18/19.7.1 and 18/19.7.2).
STANDARD
EC.02.03.03 | [6 empty] | The hospital conducts fire drills. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(b)(1)(i) |  |  |  | A |  | 1. The hospital conducts fire drills once per shift per quarter in each building defined as a health care occupancy by the Life Safety Code. The hospital conducts quarterly fire drills in each building defined as an ambulatory health care occupancy by the Life Safety Code. (See also LS.01.02.01, EP 11; LS.02.01.70, EP 4; LS.03.01.70, EP 6) Note 1: Evacuation of patients during drills is not required. Note 2: In leased or rented facilities, drills need be conducted only in areas of the building that the hospital occupies.
| §482.41(b)(7) |  |  |  | A |  | 2. The hospital conducts fire drills every 12 months from the date of the last drill in all freestanding buildings classified as business occupancies and in which patients are seen or treated. Note: In leased or rented facilities, drills need be conducted only in areas of the building that the hospital occupies.
| §482.41(b)(1)(i) |  |  |  | A |  | 3. When quarterly fire drills are required, at least 50% are unannounced. Fire drills are held at unexpected times and under varying conditions.
| §482.41(b)(1)(i) | M |  |  | C |  | 4. Staff who work in buildings where patients are housed or treated participate in drills according to the hospital’s fire response plan. Note: When drills are conducted between 9:00 p.m. and 6:00 a.m., the hospital may use alternative methods to notify staff instead of activating audible alarms.
| §482.41(b)(1)(i) |  |  | D | A |  | 5. The hospital critiques fire drills to evaluate fire safety equipment, fire safety building features, and staff response to fire. The evaluation is documented. (See also EC.02.03.01, EP 10)
STANDARD
EC.02.03.05 | [6 empty] | The hospital maintains fire safety equipment and fire safety building features. Note: This standard does not require hospitals to have the types of fire safety equipment and building features described below. However, if these types of equipment or features exist within the building, then the following maintenance, testing, and inspection requirements apply. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(c)(2) |  |  | D | A |  | 1. At least quarterly, the hospital tests supervisory signal devices (except valve tamper switches). The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 72, 1999 edition (Table 7-3.2).
| §482.41(c)(2) |  |  | D | A |  | 2. For hospitals that use Joint Commission accreditation for deemed status purposes: At least quarterly, the hospital tests water-flow devices. Every 6 months, the hospital tests valve tamper switches. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition (Sections 2-3.3 and 3-3.3) and NFPA 72, 1999 edition (Table 7-3.2). For hospitals that do not use Joint Commission accreditation for deemed status purposes: Every 6 months, the hospital tests valve tamper switches and water-flow devices. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 72, 1999 edition (Table 7-3.2).
| §482.41(c)(2) |  |  | D | C |  | 3. Every 12 months, the hospital tests duct detectors, electromechanical releasing devices, heat detectors, manual fire alarm boxes, and smoke detectors. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 72, 1999 edition (Table 7-3.2).
| §482.41(c)(2) |  | 3 | D | C |  | 4. Every 12 months, the hospital tests visual and audible fire alarms, including speakers. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 72, 1999 edition (Table 7-3.2).
| §482.41(c)(2) |  |  | D | A |  | 5. Every quarter, the hospital tests fire alarm equipment for notifying off-site fire responders. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 72, 1999 edition (Table 7-3.2).
| §482.41(c)(2) | M |  | D | C |  | 6. For automatic sprinkler systems: Every week, the hospital tests fire pumps under no-flow conditions. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition.
| §482.41(c)(2) |  |  | D | A |  | 7. For automatic sprinkler systems: Every 6 months, the hospital tests water-storage tank high- and low-water level alarms. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition (Section 6-3.5).
| §482.41(c)(2) | M |  | D | C |  | 8. For automatic sprinkler systems: Every month during cold weather, the hospital tests water-storage tank temperature alarms. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition (Section 6-3).
| §482.41(c)(2) |  |  | D | A |  | 9. For automatic sprinkler systems: Every 12 months, the hospital tests main drains at system low point or at all system risers. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition (Section 9-2.6).
| §482.41(c)(2) |  |  | D | A |  | 10. For automatic sprinkler systems: Every quarter, the hospital inspects all fire department water supply connections. The completion dates of the inspections are documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition (Section 9-7.1).
| §482.41(c)(2) |  | 3 | D | A |  | 11. For automatic sprinkler systems: Every 12 months, the hospital tests fire pumps under flow. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition.
| §482.41(c)(2) |  |  | D | A |  | 12. Every 5 years, the hospital conducts water-flow tests for standpipe systems. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 25, 1998 edition.
| §482.41(c)(2) |  |  | D | A |  | 13. Every 6 months, the hospital inspects any automatic fire-extinguishing systems in a kitchen. The completion dates of the inspections are documented. Note 1: Discharge of the fire-extinguishing systems is not required. Note 2: For additional guidance on performing inspections, see NFPA 96, 1998 edition.
| §482.41(c)(2) |  |  | D | A |  | 14. Every 12 months, the hospital tests carbon dioxide and other gaseous automatic fire-extinguishing systems. The completion date of the tests is documented. Note: Discharge of the fire-extinguishing systems is not required.
| §482.41(c)(2) | M |  | D | C |  | 15. At least monthly, the hospital inspects portable fire extinguishers. The completion dates of the inspections are documented. Note 1: There are many ways to document the inspections, such as using bar-coding equipment, using check marks on a tag, or using an inventory. Note 2: Inspections involve a visual check for the presence and correct type of extinguisher, broken parts, full charge, and ease of access. Note 3: For additional guidance on inspection of fire extinguishers, see NFPA 10, Standard for Portable Fire Extinguishers, 1998 edition (Sections 1-6, 4-3, and 4-4).
| §482.41(c)(2) |  |  | D | A |  | 16. Every 12 months, the hospital performs maintenance on portable fire extinguishers. The completion date of the maintenance is documented. Note 1: There are many ways to document the maintenance, such as using bar-coding equipment, using check marks on a tag, or using an inventory. Note 2: For additional guidance on maintaining fire extinguishers, see NFPA 10, 1998 edition (Sections 1-6, 4-3, and 4-4).
| §482.41(c)(2) |  |  | D | A |  | 17. The hospital conducts hydrostatic tests on standpipe occupant hoses 5 years after installation and every 3 years thereafter. The completion date of the tests is documented. Note: For additional guidance on hydrostatic testing, see NFPA 1962, 1998 edition (Section 2-3), and NFPA 25, 1998 edition.
| §482.41(c)(2) |  |  | D | C |  | 18. The hospital operates fire and smoke dampers 1 year after installation and then at least every 6 years to verify that they fully close. The completion date of the tests is documented. Note 1: The initial test that must occur 1 year after installation applies only to dampers installed on and after January 1, 2008. Note 2: For additional guidance, see NFPA 80 Standard for Fire Doors and Other Opening Protectives, 2007 edition (Section 19.4.1.1) and NFPA 105, 2007 edition (Section 6.5.2).
| §482.41(c)(2) |  | 3 | D | A |  | 19. Every 12 months, the hospital tests automatic smoke-detection shutdown devices for air-handling equipment. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 90A, Standard for the Installation of Air Conditioning and Ventilation Systems, 1999 edition (Section 4-4.1).
| §482.41(c)(2) |  |  | D | A |  | 20. Every 12 months, the hospital tests sliding and rolling fire doors for proper operation and full closure. The completion date of the tests is documented. Note: For additional guidance on performing tests, see NFPA 80, 1999 edition (Section 15-2.4).
| §482.41(b)(1)(i) |  |  | D | C |  | 25. For hospitals that use Joint Commission accreditation for deemed status purposes: Documentation of maintenance, testing, and inspection activities for fire alarm and water-based fire protection systems includes the following: - Name of the activity - Date of the activity - Required frequency of the activity - Name and contact information, including affiliation, of the person who performed the activity - NFPA standard(s) referenced for the activity - Results of the activity Note: For additional guidance on documenting activities, see NFPA 25, 1998 edition (Section 2-1.3) and NFPA 72, 1999 edition (Section 7-5.2).
STANDARD
EC.02.04.01 | [6 empty] | The hospital manages medical equipment risks. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
[5 empty] | A |  | 1. The hospital solicits input from individuals who operate and service equipment when it selects and acquires medical equipment.
| §482.26(b)(2) §482.41(c)(2) |  |  | D | C | ESP-1 | 2. For hospitals that do not use Joint Commission accreditation for deemed status purposes: The hospital maintains either a written inventory of all medical equipment or a written inventory of selected equipment categorized by physical risk associated with use (including all life-support equipment) and equipment incident history. The hospital evaluates new types of equipment before initial use to determine whether they should be included in the inventory. (See also EC.02.04.03, EPs 1 and 3) For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital maintains a written inventory of all medical equipment. (See also EC.02.04.03, EPs 1 and 3)
| §482.41(c)(2) |  |  | D | C | ESP-1 | 3. The hospital identifies high-risk medical equipment on the inventory for which there is a risk of serious injury or death to a patient or staff member should the equipment fail. Note: High-risk medical equipment includes life-support equipment.
| §482.26(b)(2) §482.41(c)(2) §482.53(c)(1) |  |  | D | C | ESP-1 | 4. The hospital identifies the activities and associated frequencies, in writing, for maintaining, inspecting, and testing all medical equipment on the inventory. These activities and associated frequencies are in accordance with manufacturers’ recommendations or with strategies of an alternative equipment maintenance (AEM) program. Note: The strategies of an AEM program must not reduce the safety of equipment and must be based on accepted standards of practice. * Footnote *: An example of standards for a medical equipment program is the American National Standards Institute/Association for the Advancement of Medical Instrumentation handbook ANSI/AAMI EQ56: 2013, Recommended Practice for a Medical Equipment Management Program.
| §482.41(c)(2) |  |  | D | A | ESP-1 | 5. For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital’s activities and frequencies for inspecting, testing, and maintaining the following items must be in accordance with manufacturers’ recommendations: - Equipment subject to federal or state law or Medicare Conditions of Participation in which inspecting, testing, and maintaining must be in accordance with the manufacturers’ recommendations, or otherwise establishes more stringent maintenance requirements - Medical laser devices - Imaging and radiologic equipment (whether used for diagnostic or therapeutic purposes) - New medical equipment with insufficient maintenance history to support the use of alternative maintenance strategies Note: Maintenance history includes any of the following documented evidence: - Records provided by the hospital’s contractors - Information made public by nationally recognized sources - Records of the hospital’s experience over time
| §482.41(c)(2) |  |  | D | A | ESP-1 | 6. For hospitals that use Joint Commission accreditation for deemed status purposes: A qualified individual(s) uses written criteria to support the determination whether it is safe to permit medical equipment to be maintained in an alternate manner that includes the following: - How the equipment is used, including the seriousness and prevalence of harm during normal use - Likely consequences of equipment failure or malfunction, including seriousness of and prevalence of harm - Availability of alternative or back-up equipment in the event the equipment fails or malfunctions - Incident history of identical or similar equipment - Maintenance requirements of the equipment (For more information on defining staff qualifications, refer to Standard HR.01.02.01)
| §482.41(c)(2) |  |  | D | C | ESP-1 | 7. For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital identifies medical equipment on its inventory that is included in an alternative equipment maintenance program.
| §482.41(c)(2) |  |  |  | A |  | 8. The hospital monitors and reports all incidents in which medical equipment is suspected in or attributed to the death, serious injury, or serious illness of any individual, as required by the Safe Medical Devices Act of 1990.
| §482.41(a) §482.41(c)(2) |  | 3 | D | A | ESP-1 | 9. The hospital has written procedures to follow when medical equipment fails, including using emergency clinical interventions and backup equipment.
STANDARD
EC.02.04.03 | [6 empty] | The hospital inspects, tests, and maintains medical equipment. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.26(b)(1) §482.26(b)(2) §482.41(c)(2) §482.53(c)(1) |  | 3 |  | C |  | 1. For hospitals that do not use Joint Commission accreditation for deemed status purposes: Before initial use of medical equipment on the medical equipment inventory, the hospital performs safety, operational, and functional checks. (See also EC.02.04.01, EP 2) For hospitals that use Joint Commission accreditation for deemed status purposes: Before initial use and after major repairs or upgrades of medical equipment on the medical equipment inventory, the hospital performs safety, operational, and functional checks. (See also EC.02.04.01, EP 2)
| §482.41(c)(2) |  | 3 | D | A |  | 2. The hospital inspects, tests, and maintains all high-risk equipment. These activities are documented. (See also EC.02.04.01, EPs 3 and 4; PC.02.01.11, EP 2) Note: High-risk medical equipment includes life-support equipment.
| §482.26(b)(1) §482.26(b)(2) §482.41(c)(2) §482.53(c)(1) | M |  | D | C |  | 3. The hospital inspects, tests, and maintains non–high-risk equipment identified on the medical equipment inventory. These activities are documented. (See also EC.02.04.01, EPs 2 and 4)
| §482.41(c)(2) |  | 3 | D | A |  | 4. The hospital conducts performance testing of and maintains all sterilizers. These activities are documented. (See also IC.02.02.01, EP 2)
| §482.41(c)(2) |  | 3 | D | A |  | 5. The hospital performs equipment maintenance and chemical and biological testing of water used in hemodialysis. These activities are documented.
| §482.53(c)(2) |  |  | D | A |  | 14. For hospitals that use Joint Commission accreditation for deemed status purposes: Qualified hospital staff inspect, test, and calibrate nuclear medicine equipment annually. The dates of these activities are documented.
|  | M | 3 | D | A |  | 17. For hospitals in California that provide computed tomography (CT) services: A qualified medical physicist measures the actual radiation dose * produced by each diagnostic CT imaging system at least annually and verifies that the radiation dose displayed on the system for standard adult brain, adult abdomen, and pediatric brain protocols is within 20 percent of the actual amount of radiation dose delivered. The dates of these verifications are documented. Note: This element of performance is applicable only for systems capable of calculating and displaying radiation doses. Footnote *: For the definition of “radiation dose” refer to section 115111(f) of the California Health and Safety Code.
STANDARD
EC.02.05.01 | [6 empty] | The hospital manages risks associated with its utility systems. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41 |  |  |  | A | ESP-1 | 1. The hospital designs and installs utility systems that meet patient care and operational needs. (See also EC.02.06.05, EP 1)
| §482.41(c)(2) |  |  | D | C | ESP-1 | 2. For hospitals that do not use Joint Commission accreditation for deemed status purposes: The hospital maintains a written inventory of all operating components of utility systems or maintains a written inventory of selected operating components of utility systems based on risks for infection, occupant needs, and systems critical to patient care (including all life-support systems). The hospital evaluates new types of utility components before initial use to determine whether they should be included in the inventory. (See also EC.02.05.05, EPs 1, 3–5) For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital maintains a written inventory of all operating components of utility systems. (See also EC.02.05.05, EPs 1, 3–5)
| §482.41(c)(2) |  |  | D | C | ESP-1 | 4. The hospital identifies high-risk operating components of utility systems on the inventory for which there is a risk of serious harm or death to a patient or staff member should the component fail. Note: High-risk utility system components include life-support equipment.
| §482.41(c)(2) |  |  | D | A | ESP-1 | 5. For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital’s activities and frequencies for inspecting, testing, and maintaining the following items must be in accordance with manufacturers’ recommendations: - Equipment subject to federal or state law or Medicare Conditions of Participation in which inspecting, testing, and maintaining be in accordance with the manufacturers’ recommendations, or otherwise establishes more stringent maintenance requirements - New operating components with insufficient maintenance history to support the use of alternative maintenance strategies Note: Maintenance history includes any of the following documented evidence: - Records provided by the hospital’s contractors - Information made public by nationally recognized sources - Records of the hospital’s experience over time
| §482.41(c)(2) |  |  | D | A | ESP-1 | 6. For hospitals that use Joint Commission accreditation for deemed status purposes: A qualified individual(s) uses written criteria to support the determination whether it is safe to permit operating components of utility systems to be maintained in an alternate manner that includes the following: - How the equipment is used, including the seriousness and prevalence of harm during normal use - Likely consequences of equipment failure or malfunction, including seriousness of and prevalence of harm - Availability of alternative or back-up equipment in the event the equipment fails or malfunctions - Incident history of identical or similar equipment - Maintenance requirements of the equipment (For more information on defining staff qualifications, refer to Standard HR.01.02.01)
| §482.41(c)(2) |  |  | D | C | ESP-1 | 7. For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital identifies operating components of utility systems on its inventory that is included in an alternative equipment maintenance program.
| §482.41(a) |  |  |  | A | ESP-1 | 8. The hospital labels utility system controls to facilitate partial or complete emergency shutdowns.
| §482.41(a) §482.41(a)(2) |  |  | D | A | ESP-1 | 9. The hospital has written procedures for responding to utility system disruptions.
| §482.41(a) §482.41(a)(2) §482.41(c)(2) |  |  |  | A | ESP-1 | 10. The hospital's procedures address shutting off the malfunctioning system and notifying staff in affected areas.
| §482.41(a) §482.41(a)(2) |  |  |  | A | ESP-1 | 11. The hospital's procedures address performing emergency clinical interventions during utility system disruptions.
| §482.41(a) §482.41(a)(2) |  |  |  | A | ESP-1 | 12. The hospital's procedures address how to obtain emergency repair services.
| §482.41(a) §482.41(a)(2) |  | 3 |  | A |  | 13. The hospital responds to utility system disruptions as described in its procedures.
| §482.42 |  | 3 |  | A |  | 14. The hospital minimizes pathogenic biological agents in cooling towers, domestic hot- and cold-water systems, and other aerosolizing water systems.
| §482.42 |  | 3 |  | A | ESP-1 | 15. In areas designed to control airborne contaminants (such as biological agents, gases, fumes, dust), the ventilation system provides appropriate pressure relationships, air-exchange rates, and filtration efficiencies. (See also EC.02.06.01, EP 13) Note: Areas designed for control of airborne contaminants include spaces such as operating rooms, special procedure rooms, delivery rooms for patients diagnosed with or suspected of having airborne communicable diseases (for example, pulmonary or laryngeal tuberculosis), patients in "protective environment" rooms (for example, those receiving bone marrow transplants), laboratories, pharmacies, and sterile supply rooms. For further information, see Guidelines for Design and Construction of Health Care Facilities, 2010 edition, administered by the Facility Guidelines Institute and published by the American Society for Healthcare Engineering (ASHE).
| §482.41(a) |  |  | D | A | ESP-1 | 16. The hospital maps the distribution of its utility systems.
STANDARD
EC.02.05.03 | [6 empty] | The hospital has a reliable emergency electrical power source. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(a)(1) |  | 3 |  | A | ESP-1 | 1. The hospital provides emergency power for the following: Alarm systems, as required by the Life Safety Code. Note: For guidance in establishing a reliable emergency power system (that is, an essential electrical distribution system), see NFPA 99, 1999 edition (Section 12-3.3).
| §482.41(a)(1) |  | 3 |  | A | ESP-1 | 2. The hospital provides emergency power for the following: Exit route and exit sign illumination, as required by the Life Safety Code. Note: For guidance in establishing a reliable emergency power system (that is, an essential electrical distribution system), see NFPA 99, 1999 edition (Section 12-3.3).
| §482.41(a)(1) |  | 3 |  | A | ESP-1 | 3. The hospital provides emergency power for the following: Emergency communication systems, as required by the Life Safety Code. Note: For guidance in establishing a reliable emergency power system (that is, an essential electrical distribution system), see NFPA 99, 1999 edition (Section 12-3.3).
| §482.41(a)(1) |  |  |  | A | ESP-1 | 4. The hospital provides emergency power for the following: Elevators (at least one for nonambulatory patients). Note: For guidance in establishing a reliable emergency power system (that is, an essential electrical distribution system), see NFPA 99, 1999 edition (Section 12-3.3).
| §482.41(a)(1) |  | 3 |  | A | ESP-1 | 5. The hospital provides emergency power for the following: Equipment that could cause patient harm when it fails, including life-support systems; blood, bone, and tissue storage systems; medical air compressors; and medical and surgical vacuum systems. Note: For guidance in establishing a reliable emergency power system (that is, an essential electrical distribution system), see NFPA 99, 1999 edition (Section 12-3.3).
| §482.41(a)(1) |  | 3 |  | A | ESP-1 | 6. The hospital provides emergency power for the following: Areas in which loss of power could result in patient harm, including intensive care, emergency rooms, operating rooms, recovery rooms, obstetrical delivery rooms, nurseries, and urgent care areas. Note: For guidance in establishing a reliable emergency power system (that is, an essential electrical distribution system), see NFPA 99, 1999 edition (Section 12-3.3).
STANDARD
EC.02.05.05 | [6 empty] | The hospital inspects, tests, and maintains utility systems. Note: At times, maintenance is performed by an external service. In these cases, hospitals are not required to possess maintenance documentation but must have access to such documentation during survey and as needed. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(c)(2) |  |  | D | C | ESP-1 | 1. For hospitals that do not use Joint Commission accreditation for deemed status purposes: The hospital tests utility system components on the inventory before initial use. The completion date of the tests is documented. (See also EC.02.05.01, EP 2) For hospitals that use Joint Commission accreditation for deemed status purposes: The hospital tests utility system components on the inventory before initial use and after major repairs or upgrades. The completion date of the tests is documented. (See also EC.02.05.01, EP 2)
| §482.41(c)(2) |  | 3 | D | A |  | 3. The hospital inspects, tests, and maintains the following: High-risk utility system components on the inventory. These activities are documented. (See also EC.02.05.01, EPs 2 and 4) Note: High-risk utility system components includes life-support utility system components.
| §482.41(c)(2) §482.42 |  | 3 | D | A |  | 4. The hospital inspects, tests, and maintains the following: Infection control utility system components on the inventory. These activities are documented. (See also EC.02.05.01, EPs 2 and 4)
| §482.41(c)(2) | M |  | D | C |  | 5. The hospital inspects, tests, and maintains the following: Non–high-risk utility system components on the inventory. These activities are documented. (See also EC.02.05.01, EPs 2 and 4)
STANDARD
EC.02.05.07 | [6 empty] | The hospital inspects, tests, and maintains emergency power systems. Note: This standard does not require hospitals to have the types of emergency power equipment discussed below. However, if these types of equipment exist within the building, then the following maintenance, testing, and inspection requirements apply. Rationale: Emergency electrical power supply systems may fail during a power disruption, leaving the hospital unable to deliver safe care, treatment, and services to patients. Testing these systems for sufficient lengths of time at regular frequencies increases the likelihood of detecting reliability problems and reduces the risk of losing this critical resource when it is most needed. Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(b)(4) | M |  | D | C |  | 1. At least monthly, the hospital performs a functional test of battery-powered lights required for egress for a minimum duration of 30 seconds. The completion date of the tests is documented.
| §482.41(b)(4) |  |  | D | C |  | 2. Every 12 months, the hospital either performs a functional test of battery-powered lights required for egress for a duration of 1 1/2 hours; or the hospital replaces all batteries every 12 months and, during replacement, performs a random test of 10% of all batteries for 1 1/2 hours. The completion date of the tests is documented.
| §482.41(c)(2) |  |  | D | A |  | 3. Every quarter, the hospital performs a functional test of stored emergency power supply systems (SEPSS) for 5 minutes or as specified for its class (whichever is less). The hospital performs an annual test at full load for 60% of the full duration of its class. The completion dates of the tests are documented. Note 1: Non–SEPSS battery backup emergency power systems that the hospital has determined to be critical for operations during a power failure (for example, laboratory equipment or electronic medical records) should be properly tested and maintained in accordance with manufacturer’s recommendations. Note 2: SEPSS are intended to automatically supply illumination or power to critical areas and equipment essential for safety to human life. Included are systems that supply emergency power for such functions as illumination for safe exiting, ventilation where it is essential to maintain life, fire detection and alarm systems, public safety communications systems, and processes where the current interruption would produce serious life safety or health hazards to patients, the public, or staff. Note 3: Class defines the minimum time for which the SEPSS is designed to operate at its rated load without being recharged. For additional guidance, see NFPA 111, Standard on Stored Electrical Energy Emergency and Standby Power Systems, 1996 edition.
- FSA Direct Impact EPs | §482.41(c)(2) |  | 3 | D | A |  | 4. At least monthly, the hospital tests each emergency generator under load for at least 30 continuous minutes. The completion dates of the tests are documented.
- FSA Direct Impact EPs | §482.41(c)(2) |  | 3 |  | A |  | 5. The monthly tests for diesel-powered emergency generators are conducted with a dynamic load that is at least 30% of the nameplate rating of the generator or meets the manufacturer’s recommended prime movers’ exhaust gas temperature. If the hospital does not meet either the 30% of nameplate rating or the recommended exhaust gas temperature during any test in EC.02.05.07, EP 4, then it must test the emergency generator once every 12 months using supplemental (dynamic or static) loads of 25% of nameplate rating for 30 minutes, followed by 50% of nameplate rating for 30 minutes, followed by 75% of nameplate rating for 60 minutes, for a total of 2 continuous hours. Note: Tests for non–diesel-powered generators need only be conducted with available load.
- FSA Direct Impact EPs | §482.41(c)(2) |  | 3 | D | A |  | 6. At least monthly, the hospital tests all automatic transfer switches. The completion date of the tests is documented.
- FSA Direct Impact EPs | §482.41(c)(2) |  | 3 | D | A |  | 7. At least once every 36 months, hospitals with a generator providing emergency power for the services listed in EC.02.05.03, EPs 5 and 6, test each emergency generator for a minimum of 4 continuous hours. The completion date of the tests is documented. Note: For additional guidance, see NFPA 110, 2005 edition, Standard for Emergency & Standby Power Systems.
- FSA Direct Impact EPs | §482.41(c)(2) |  | 3 |  | A |  | 8. The 36-month diesel-powered emergency generator test uses a dynamic or static load that is at least 30% of the nameplate rating of the generator or meets the manufacturer’s recommended prime movers' exhaust gas temperature. Note: Tests for non–diesel-powered generators need only be conducted with available load.
|  |  | 3 |  | A |  | 9. If a required emergency power system test fails, the hospital implements measures to protect patients, visitors, and staff until necessary repairs or corrections are completed.
[5 empty] | A | ESP-1 | 10. If a required emergency power system test fails, the hospital performs a retest after making the necessary repairs or corrections.
STANDARD
EC.02.05.09 | [6 empty] | The hospital inspects, tests, and maintains medical gas and vacuum systems. Note: This standard does not require hospitals to have the medical gas and vacuum systems discussed below. However, if a hospital has these types of systems, then the following inspection, testing, and maintenance requirements apply. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(c)(2) |  | 3 | D | A |  | 1. In time frames defined by the hospital, the hospital inspects, tests, and maintains critical components of piped medical gas systems, including master signal panels, area alarms, automatic pressure switches, shutoff valves, flexible connectors, and outlets. These activities are documented. (See also EC.02.05.01, EP 3)
| §482.41(c)(2) |  | 3 | D | A |  | 2. The hospital tests piped medical gas and vacuum systems for purity, correct gas, and proper pressure when these systems are installed, modified, or repaired. The completion date of the tests is documented.
| §482.41(c)(2) |  |  |  | A | ESP-1 | 3. The hospital makes main supply valves and area shutoff valves for piped medical gas and vacuum systems accessible and clearly identifies what the valves control.
STANDARD
EC.02.06.01 | [6 empty] | The hospital establishes and maintains a safe, functional environment. Note: The environment is constructed, arranged, and maintained to foster patient safety, provide facilities for diagnosis and treatment, and provide for special services appropriate to the needs of the community. Rationale: Not applicable Introduction: Introduction to Standard EC.02.06.01 Features of the hospital’s space influence patient outcomes and satisfaction and promote patient safety. The physical space also affects families, staff, and others in the organization. These features of the environment of care include the following: - Quality of natural and artificial light - Privacy - Size and configuration of space - Security for patients and their belongings - Clear access to internal and external doors - Level of noise - Space that allows staff to work efficiently When designed into and managed as part of the environment, these elements create safe and suitable surroundings that support patient dignity and allow ease of interaction. The standards do not specifically address all these features. However, organizations may wish to consider these aspects of the environment when they design and manage spaces. Decisions on what features to pursue should be based on data, such as patient satisfaction information, data collected from staff, and evidence-based design guidelines.
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41 §482.41(a) | M |  |  | C | ESP-1 | 1. Interior spaces meet the needs of the patient population and are safe and suitable to the care, treatment, and services provided.
| §482.41 §482.41(c)(4) |  |  |  | C | ESP-1 | 11. Lighting is suitable for care, treatment, and services.
| §482.41 §482.41(c)(4) |  |  |  | A | ESP-1 | 13. The hospital maintains ventilation, temperature, and humidity levels suitable for the care, treatment, and services provided. (See also EC.02.05.01, EP 15)
| §482.41 §482.42 | M | 3 |  | C | ESP-1 | 20. Areas used by patients are clean and free of offensive odors.
| §482.41 |  | 3 |  | A | ESP-1 | 23. The hospital provides emergency access to all locked and occupied spaces.
| §482.41 §482.41(a) | M |  |  | C | ESP-1 | 26. The hospital keeps furnishings and equipment safe and in good repair.
STANDARD
EC02.06.05 | [6 empty] | The hospital manages its environment during demolition, renovation, or new construction to reduce risk to those in the organization. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41 |  |  |  | A |  | 1. When planning for new, altered, or renovated space, the hospital uses one of the following design criteria: - State rules and regulations - Guidelines for Design and Construction of Health Care Facilities, 2010 edition, administered by the Facility Guidelines Institute and published by the American Society for Healthcare Engineering (ASHE) When the above rules, regulations, and guidelines do not meet specific design needs, use other reputable standards and guidelines that provide equivalent design criteria. (See also EC.02.05.01, EP 1)
| §482.41 §482.42 |  |  |  | A |  | 2. When planning for demolition, construction, or renovation, the hospital conducts a preconstruction risk assessment for air quality requirements, infection control, utility requirements, noise, vibration, and other hazards that affect care, treatment, and services. Note: See LS.01.02.01 for information on fire safety procedures to implement during construction or renovation.
| §482.41 §482.42 |  | 3 |  | A |  | 3. The hospital takes action based on its assessment to minimize risks during demolition, construction, or renovation.
STANDARD
EC.03.01.01 | [6 empty] | Staff and licensed independent practitioners are familiar with their roles and responsibilities relative to the environment of care. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(b)(1)(i) | M |  |  | C |  | 1. Staff and licensed independent practitioners can describe or demonstrate methods for eliminating and minimizing physical risks in the environment of care. (See also HR.01.04.01, EP 1)
| §482.41(b)(1)(i) | M |  |  | C |  | 2. Staff and licensed independent practitioners can describe or demonstrate actions to take in the event of an environment of care incident. (See also EC.02.03.01, EP 10 and HR.01.04.01, EP 1)
| §482.41(b)(1)(i) | M |  |  | C |  | 3. Staff and licensed independent practitioners can describe or demonstrate how to report environment of care risks. (See also HR.01.04.01, EP 1)
STANDARD
EC.04.01.01 | [6 empty] | The hospital collects information to monitor conditions in the environment. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.13(c)(2) §482.41(c)(2) |  |  |  | A | ESP-1 | 1. The hospital establishes a process(es) for continually monitoring, internally reporting, and investigating the following: - Injuries to patients or others within the hospital’s facilities - Occupational illnesses and staff injuries - Incidents of damage to its property or the property of others - Security incidents involving patients, staff, or others within its facilities - Hazardous materials and waste spills and exposures - Fire safety management problems, deficiencies, and failures - Medical or laboratory equipment management problems, failures, and use errors - Utility systems management problems, failures, or use errors Note 1: All the incidents and issues listed above may be reported to staff in quality assessment, improvement, or other functions. A summary of such incidents may also be shared with the person designated to coordinate safety management activities. Note 2: Review of incident reports often requires that legal processes be followed to preserve confidentiality. Opportunities to improve care, treatment, or services, or to prevent similar incidents, are not lost as a result of following the legal process.
| §482.41(c)(2) | M |  |  | C |  | 3. Based on its process(es), the hospital reports and investigates the following: Injuries to patients or others in the hospital’s facilities. (See also EC.04.01.03, EP 1)
|  | M |  |  | C |  | 4. Based on its process(es), the hospital reports and investigates the following: Occupational illnesses and staff injuries. (See also EC.04.01.03, EP 1)
|  | M |  |  | C |  | 5. Based on its process(es), the hospital reports and investigates the following: Incidents of damage to
| §482.13(c)(2) | M |  |  | C |  | 6. Based on its process(es), the hospital reports and investigates the following: Security incidents
| §482.26(b)(2) | M |  |  | C |  | 8. Based on its process(es), the hospital reports and investigates the following: Hazardous materials and waste spills and exposures. (See also EC.04.01.03, EP 1)
| §482.41(c)(2) | M |  |  | C |  | 9. Based on its process(es), the hospital reports and investigates the following: Fire safety management problems, deficiencies, and failures. (See also EC.04.01.03, EP 1)
| §482.41(c)(2) | M |  |  | C |  | 10. Based on its process(es), the hospital reports and investigates the following: Medical/laboratory equipment management problems, failures, and use errors. (See also EC.04.01.03, EP 1)
| §482.41(c)(2) | M |  |  | C |  | 11. Based on its process(es), the hospital reports and investigates the following: Utility systems management problems, failures, or use errors. (See also EC.04.01.03, EP 1)
| §482.26(b) §482.41(a) |  |  |  | A |  | 12. The hospital conducts environmental tours every six months in patient care areas to evaluate the effectiveness of previously implemented activities intended to minimize or eliminate environment of care risks. (See also EC.04.01.03, EP 1)
| §482.41(a) | M |  |  | C |  | 13. The hospital conducts annual environmental tours in nonpatient care areas to evaluate the effectiveness of previously implemented activities intended to minimize or eliminate risks in the environment. (See also EC.04.01.03, EP 1)
| §482.26(b) §482.41(a) |  |  |  | A |  | 14. The hospital uses its tours to identify environmental deficiencies, hazards, and unsafe practices. (See also EC.02.01.01, EP 1; EC.04.01.03, EP 1)
| §482.41(a) §482.41(c)(2) |  | 3 |  | A |  | 15. Every 12 months, the hospital evaluates each environment of care management plan, including a review of the plan’s objectives, scope, performance, and effectiveness. (See also EC.01.01.01, EPs 3-8; EC.04.01.03, EP 1)
STANDARD
EC.04.01.03 | [6 empty] | The hospital analyzes identified environment of care issues. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(c)(2) |  |  |  | A |  | 1. Representatives from clinical, administrative, and support services participate in the analysis of environment of care data. (See also EC.04.01.01, EPs 3-6 and 8-15; EC.04.01.05, EP 3)
| §482.41(a) §482.41(c)(2) | M |  |  | C |  | 2. The hospital uses the results of data analysis to identify opportunities to resolve environmental safety issues. (See also EC.04.01.05, EP 1)
[5 empty] | A |  | 3. Annually, representatives from clinical, administrative, and support services recommend one or more priorities for improving the environment of care.
STANDARD
EC.04.01.05 | [6 empty] | The hospital improves its environment of care. Rationale: Not applicable Introduction: Not applicable
Compliant Y/N | CMS | MOS | CR | DOC | SC | ESP | Elements of Performance | Title 22 | MLKCH Validation | Person Responsible
| §482.41(a) §482.41(c)(2) | M |  |  | C |  | 1. The hospital takes action on the identified opportunities to resolve environmental safety issues. (See also EC.04.01.03, EP 2)
|  | M |  |  | C |  | 2. The hospital evaluates changes to determine if they resolved environmental safety issues.
| §482.41(c)(2) |  |  |  | A |  | 3. The hospital reports performance improvement results to those responsible for analyzing environment of care issues. (See also EC.04.01.03, EP 1; EM.03.01.03, EP 15)